· Suffix code

| Model |  | Code |  | Information |  |
| --- | --- | --- | --- | --- | --- |
| AX | - |  |  | Digital temperature controller |  |
| Dimension | 2 |  |  | AX2 : 48 X 96 mm |  |
|  | 3 |  |  | AX3 : 96 X 48 mm |  |
|  | 4 |  |  | AX4 : 48 X 48 mm |  |
|  | 7 |  |  | AX7 : 72 X 72 mm |  |
|  | 9 |  |  | AX9 : 96 X 96 mm |  |
| Output selection |  | 1 |  | SSR + Relay1 + Relay2 | Relay or SSR as control output (selectable in operator setup mode) |
|  |  | 2 |  | SSR + Relay1 + Relay2 + Relay3 |  |
|  |  | 1B |  | SSR + Relay1(Form c) + Relay2 | Only for AX2, 3, 7, 9 |
|  |  | 2B |  | SSR + Relay1(Form c) + Relay2 + Relay3 |  |
|  |  | 3 |  | 4 - 20 ㎃ + Relay2 | Current output as control output |
|  |  | 4 |  | 4 - 20 ㎃ + Relay2 + Relay3 |  |
| Power supply voltage |  |  | A | 100 - 240 V a.c 50/60 ㎐ |  |

※ Form C : Normal close type contact

※ Relay output operates as control output, alarm output and LBA output depending on the internal parameter setting.

· Specification

| Appearance |  | AX4 | AX3 | AX7 | AX2 | AX9 |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 48 X 48 X 63 | 96 X 48 X 63 | 72 X 72 X 63 | 48 X 96 X 63 | 96 X 96 X 63 |
| Input type |  | Multi input(Thermocouple : K, J, R, T, IEC 584-1), (RTD : Pt100 Ω, IEC751) |  |  |  |  |
| Sampling cycle |  | 100 ms |  |  |  |  |
| Input impedance |  | max 1 ㏁ |  |  |  |  |
| Albwable input wiring resistance |  | 10 V DC |  |  |  |  |
| Display accuracy | Thermocouple K,J,T | ± 0.3 % of F.S ±1 digit (RJC error ±0.8%) ℃ |  |  |  |  |
|  | Thermocouple R | ±1.0% of F.S ±1 digit in the 0 ~ 600 ℃ range |  |  |  | ± 2.0℃ in the range of 0~600℃, ± 0.8℃ outside of the range |
|  |  | ±0.3 % F.S ±1 digit in the 600 ~ 1700 ℃ range |  |  |  |  |
|  | Pt100 | ±0.3 % of F.S ±1 digit℃ |  |  |  |  |
| Display type |  | 7 Segment LED (PV : red, SV : green) |  |  |  |  |
| Font size | PV | 13.0 X 6.5 | 15.9 X 7.6 | 14.5 X 7.0 | 14.5 X 7.0 | 22.5 X 11.2 |
|  | SV | 9.2 X 5.2 | 12.0 X 6.0 | 9.4 X 4.7 | 10.8 X 5.2 | 18.7 X 9.3 |
| Input resolving power |  | - • Thermocouple : 0.1℃ (K2, J, T), 0.5℃ (K1), 0.3℃ / 1℉ (R) - • RTD : 0.03℃, (0.1 ℉) |  |  |  |  |
| Insulation resistance |  | min 20㏁, 500 V DC 1 minute (primary terminal - secondary terminal) |  |  |  |  |
| Dielectric strength |  | 2,300 V AC, 50/60 ㎐, for 1min (primary terminal - secondary terminal) |  |  |  |  |
| Control method |  | PID control by Auto-tuning, ON/OFF control |  |  |  |  |
| Manual reset |  | Users set with in the range 0.0% - 100.0% |  |  |  |  |
| Control output operation |  | Reverse operation / Direct operation selectable by the parameter setting |  |  |  |  |
| Control output |  | - • Relay output ※Selectable by the prameter setting 1a contact, 3 A 240 V AC, 3 A 30 V DC(resistive load) |  |  |  |  |
|  |  | - • Voltage pluse output for running SSR [time sharing proportional control (CYC)] - • Voltage plus output for running SSR [phase control(PHR)] 0/12 V DC, pulse voltage (resistive load minimum 600Ω) |  |  |  |  |
|  |  | 4 - 20 ㎃ DC(resistive load max. 600Ω) |  |  |  |  |
| Power supply voltage |  | 100 - 240 V AC 50 / 60 ㎐ |  |  |  |  |
| Voltage fluctuation |  | ±10 % of the power supply voltage |  |  |  |  |
| Power consumption |  | 5.5 VA max |  |  |  |  |
| Ambient temperature |  | -5 ~ 50℃ |  |  |  |  |
| Ambient humidity |  | 35 ~ 85% RH (without condensation) |  |  |  |  |
| Vibration resistance |  | 10 -55 ㎐, 0.75 mm, each to direction, X, Y and Z for 2 hours |  |  |  |  |
| Shock resistance |  | 300 ㎨ to direction 6 each 3 times |  |  |  |  |
| Weight |  | 180 g | 320 g | 300 g | 320 g | 400g |