Suffix code

| Model | Code | Information |
| --- | --- | --- |
| MA4N- |  | Analog multi timer (48 X 48 ㎜) |
| Device selection | A | 2c (time limit) ※11 pin type |
|  | B | 2c (time limit+ constantaneous) ※11pin type. |
|  | C | 2c (time limit), 2c (time limit+ constantaneous) ※ processed by mode selection (8pin type) |
| Power supply voltage |  | 24 - 240 V AC/DC (50 - 60 ㎐) (dual usage) |

· Specification

| Model |  | MA4N-A | MA4N-B | MA4N-C |
| --- | --- | --- | --- | --- |
| Power Supply voltage |  | 24 - 240 V a.c / d.c 50 - 60 Hz |  |  |
| Voltage regulation |  | ±10 % from supply voltage |  |  |
| Power consumption |  | 5.3 VA (240 V a.c), 2.5 W (240 V d.c) |  |  |
| Resetting time |  | Max. 0.1 sec |  |  |
| Min Signal length | START Input | Min. 20 ms |  | - |
|  | INHIBIT Input |  |  |  |
|  | RESET Input |  |  |  |
| Input condition | START Input | Non voltage Input Impedance in a short circuit : Max. 2 kΩ Residual voltage in a short circuit : Max. 0.7 V d.c Impedance in open : Min. 100 kΩ |  | - |
|  | INHIBIT Input |  |  |  |
|  | RESET Input |  |  |  |
| Output |  | Time Limit 2c | Time Limit 1c Instautaneous 1c | Time Limit 2c Time Limit 1c Instautaneous 1c |
|  |  | N.O : 10 A 125 V a.c, 5 A 250 V a.c, 5 A 30 V d.c N.C : 3 A 125 V a.c, 2 A 250 V a.c, 1 A 30 V d.c |  |  |
| Setting error |  | Max. ± 5 % ± 0.05 sec - |  |  |
| Repeat error |  | Max. ± 0.3 % |  |  |
| Temperature error |  | Max. ± 2 % |  |  |
| Insulation resistance |  | Min. 100 MΩ (Base on 500 V d.c) |  |  |
| Dielectric strength |  | 2000 V a.c 50 / 60 Hz for 1 min. |  |  |
| Impulse voltage |  | ± 2000 V Max. |  |  |
| Vibration | Mechanical Resistance | 10 - 55 Hz double amplitude 0.75 mm |  |  |
|  | Malfunction durability | 10 - 55 Hz double amplitude 0.5 mm |  |  |
| Shock | Mechanical Resistance | 300 m/s² (Approx. 30 G) |  |  |
|  | Malfunction durability | 100 m/s² (Approx. 10 G) |  |  |
| Life | Mechanical | Over 10 million operations (Open & Short frequency : 180 / min) |  |  |
|  | Electrical | Over 100,000 (250 V a.c 3 A load resistance) |  |  |
| Terminal type |  | Socket type 11 pin |  | Socket type 8 pin |
| Ambient temperature |  | -10 ~ 55 ℃ (With no condensation) |  |  |
| Conservation temperature |  | -20 ~ 65 ℃ (With no condensation) |  |  |
| Ambient humidity |  | 35 ~ 85 %R.H. |  |  |
| Weight |  | About 100g (Including fixing bracket) |  |  |